## How to use
Holiday let hot tub log
Free to copy, edit and share. By Pulad Labs (puladlabs.com/guides/). Not legal advice: follow your own risk assessment and your council's guidance.
Why: in the UK a hot tub offered to paying guests is a work activity under the Health and Safety at Work Act. HSE's guidance HSG282 lists typical checks:
- pH and disinfectant (chlorine or bromine): at least twice a day for domestic-type hot tubs, depending on your risk assessment and use.
- Water clarity and the water line: daily; water replacement between lets or as your risk assessment says.
- Microbiological samples by a lab (councils commonly ask monthly, and legionella at least quarterly).
- Keep test and check records for at least 5 years; each record should show who did it and when, and be signed or otherwise verified.
Tabs
1. Daily checks: one row per check (morning and evening). Red cells = outside the targets in the Targets tab.
2. Changeovers: water change, filter clean, cover clean between guests.
3. Lab results: monthly and quarterly samples.
4. Targets: edit to match your risk assessment.
5. Alarm tests: smoke, heat and CO alarms between guests (fire safety is a separate legal duty for paying-guest accommodation; see the gov.uk guide 'Making your small paying guest accommodation safe from fire').
6. Water flushing: run taps and showers after the property has stood empty, and spot-check temperatures (hot at least 50 C, cold below 20 C are the usual Legionella control figures; follow your own water risk assessment).
Tip: the Clearly app (Android) turns a test into the exact chemical amounts for your tub. See puladlabs.com/clearly.

## Targets
Test | Minimum | Maximum | Note
Free chlorine (mg/l) | 3 | 5 | Or bromine 4-6 mg/l; set by your risk assessment
Bromine (mg/l) | 4 | 6 | Use if you run bromine instead of chlorine
pH | 7 | 7.6 | HSG282 typical range for spa pools
Total alkalinity (mg/l) | 80 | 120
Water temperature (C) | 30 | 40 | Do not exceed 40 C

## Daily checks
Date | Time | Hot tub / property | Free chlorine (mg/l) | Bromine (mg/l) | pH | Water clear? (Y/N) | Water line clean? (Y/N) | Chemical added (what, how much) | Checked by (name) | Signed (initials) | Notes | Water temp (C) | Filter / strainers checked (Y/N)

## Changeovers
Date | Hot tub / property | Water drained and refilled? (Y/N) | Filter cleaned or changed | Cover and headrests cleaned | Shock dose added | Done by | Signed | Notes

## Lab results
Sample date | Hot tub / property | Lab | Test (ACC / coliforms / E. coli / Pseudomonas / Legionella) | Result | Within limits? (Y/N) | Action taken | Report reference | Recorded by

## Monthly
Date | Hot tub / property | Jets removed and inspected (Y/N) | Biofilm found? (Y/N) | Pipework cleaned and disinfected (Y/N) | Lab sample taken (Y/N) | Done by | Signed | Notes

## Alarm tests
Date | Property | Smoke alarms tested (Y/N) | Heat / CO alarms tested (Y/N) | Fire blanket / extinguisher present (Y/N) | Escape route clear (Y/N) | Done by | Signed | Notes

## Water flushing
Date | Property | Empty since (days) | All taps and showers run 2+ min (Y/N) | Hot water temperature at tap (C) | Cold water temperature at tap (C) | Done by | Signed | Notes